Specification
Highly-tight shut-off damper KLB
	Quantity
	Description of services
	Unit price
in €
	Total price
in €

	
	
The highly-tight shut-off damper type KLB is designed to hermetically shut off airflow.
[bookmark: _GoBack]The leakage air rate is too low to be reported when tested. 
A near perfect isolation is achieved using a "positive seal" technique whereby the blade rotates and then closes onto a peripheral seal.
For this purpose a 4-joint link mechanism is used that, from the open position, first rotates the blade by 90 °, then after a translation movement pushes it in a longitudinal direction onto the damper housing against a sealing ring.
Each damper is individually leak tested and can be rated to other relevant standards.

Consisting of:
· Casing made of 1.5 mm galvanised sheet steel, with welded flat flanges in accordance with DIN 24154 Series 3
· Shafts made of V2A stainless steel
· Shaft passage sealed with a shaft seal ring
· Maintenance-free damper bearings in PTFE bushings with bronze inserts
· EPDM seal, formaldehyde-resistant
· Manual adjustment lever

Model sizes Ø
· 224 mm
· 250 mm
· 315 mm
· 355 mm
· 400 mm
· 500 mm
· 630 mm
· 710 mm
· 800 mm
· 1000 mm

Manufacturer:	LTG Aktiengesellschaft
Series:			Shut-off dampers
Type:				KLB

Accessories, special equipment (optional, additional charge)

· V2A stainless steel version (grade 1.4301)
· V4A stainless steel version (grade 1.4571)
· Electric actuator, Schischek, type InMax-15-SF: 
Power supply: 24–240 VAC/DC, open-close / 3-stage control mode
· Electric actuator, Belimo type SFA-S2: Power supply 24–240 V AC /  
24–125 V DC, 2 auxiliary contacts, spring return with damper OPEN or CLOSED
· Leak test in accordance with specifications (standard)
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