| Quantity | Description of services | Unit price in € | Total price in € |
| --- | --- | --- | --- |
|  | The highly-tight shut-off damper type KLB is designed to hermetically shut off airflow. The leakage air rate is too low to be reported when tested. A near perfect isolation is achieved using a "positive seal" technique whereby the blade rotates and then closes onto a peripheral seal. For this purpose a 4-joint link mechanism is used that, from the open position, first rotates the blade by 90 °, then after a translation movement pushes it in a longitudinal direction onto the damper housing against a sealing ring. Each damper is individually leak tested and can be rated to other relevant standards. Consisting of: - Casing made of 1.5 mm galvanised sheet steel, with welded flat flanges in accordance with DIN 24154 Series 3 - Shafts made of V2A stainless steel - Shaft passage sealed with a shaft seal ring - Maintenance-free damper bearings in PTFE bushings with bronze inserts - EPDM seal, formaldehyde-resistant - Manual adjustment lever Model sizes Ø - 224 mm - 250 mm - 315 mm - 355 mm - 400 mm - 500 mm - 630 mm - 710 mm - 800 mm - 1000 mm Manufacturer: LTG Aktiengesellschaft Series: Shut-off dampers Type: KLB Accessories, special equipment (optional, additional charge) - V2A stainless steel version (grade 1.4301) - V4A stainless steel version (grade 1.4571) - Electric actuator, Schischek, type InMax-15-SF: Power supply: 24–240 VAC/DC, open-close / 3-stage control mode - Electric actuator, Belimo type SFA-S2: Power supply 24–240 V AC / 24–125 V DC, 2 auxiliary contacts, spring return with damper OPEN or CLOSED - Leak test in accordance with specifications (standard) |  |  |